## Slide 1: Background
Comfortable thermal indoor environments to occupants
Health
Overall satisfaction
Productivity
Extensive research on human thermal comfort since 1960s
Empirical thermal comfort models
Predicting the average comfort level
International standards (e.g., ASHRAE standard 55)

## Slide 2: Background
Comfort?
Energy?

## Slide 3: Vision
Smart and occupant-centric HVAC systems
  Building occupants in sensing/control framework (human-in-the-loop)
  Self-tuned by learning their occupants
  Optimal decisions on equipment operation
  Customized indoor environmental conditions
  Learning method
  Optimal control strategy
  HVAC equipment
  User-interface
  Sensing device
Open-plan Office
Private Office
Energy Grid
Weather
Sensor Data
Occupant Feedback
Local Sensing
- Temperature
- Occupancy
- Physiological Info.
Learning Module
- Occupant Preferences
- Occupancy Schedule
- Occupant Behavior
Control Module
- Stochastic Opt. Control
- Multi-Agent Architecture
- Distributed Optimization
Data Handling
- Weather
- Indoor Conditions
- Occupancy
- Occupant Feedback
- System Status
- Utility Price

## Slide 4
Learning Occupants’ Thermal Comfort

## Slide 5: Learning Occupants’ Thermal Preferences
Input
(e.g., environmental conditions)
Output
(e.g., Occupant’s feedback)
Model
Machine learning / data-driven modeling techniques
  Good model structure / learning algorithm
  Effective input variables
  Focused on prediction performance / accuracy
  Lack of consideration for real-world implementations

## Slide 6: Learning Occupants’ Thermal Preferences
  I have knowledge on human thermal comfort to some extent. Can I use this knowledge to compensate for the lack of data?
  Are individuals totally different from each other? Should I train a separate model for each individual from scratch?

## Slide 7: Overall Process for Learning
Developing a Generalized Model for a Large Population
Learning an Individual Occupant
1
1
Cluster 1
2
Cluster 2
3
Cluster 3
Sub-Model for Cluster 1
Sub-Model for Cluster 2
Sub-Model for Cluster 3
Based on a Large Dataset
?
?
?
?
Occupants in
the Large Dataset
Target Occupant
Mixture of Models
Introduce equations in PMV model with additional correction parameters as my prior knowledge
Hidden Value
In the model, explicitly encode my key hypothesis: “Different people prefer different thermal condition”

## Slide 8: Bayesian Modeling Approach
: Model parameters
: Data
Bayes’ Rule
Posterior probability
(Not a point estimation)
Prior probability
(prior knowledge on )
Data likelihood
Encode our prior knowledge
Quantify the model uncertainty
Easily introduce hidden (unobserved) variables
Seamlessly combine data from heterogeneous sources

## Slide 9: Generalized Thermal Preference Model
Joint probability:
.
Equations in PMV model with additional correction parameters
Linear discriminant analysis formulation
Dirichlet process (DP) prior
,
,
.

## Slide 10: Generalized Thermal Preference Model
Subset of ASHRAE RP-884 DB
  HVAC conditioned buildings in North America
  # people: 259 / # data points: 1712

## Slide 11: Generalized Thermal Preference Model
“The true values were not measured, but there are relationships between the observed and the true values.”
,
,
.
Error-in-variables

## Slide 12: Training Algorithm
  5,454 latent variables including 59 model parameters, 259 hidden characteristics
  Automatic Differentiation Variational Inference (ADVI) algorithm
  Suitable for high-dimensional problems
  Significantly faster than typical Markov chain Monte Carlo (MCMC) methods ex) Training time with 100 CPUs ≈ 1.5 hour

## Slide 13: Generalized Thermal Preference Model

## Slide 14: Personalized Thermal Preference Models
Probability of the occupant belonging to each cluster
Predicting the thermal preference of the occupant

## Slide 15: Experimental Study
Location: 3 south-facing private offices
Period: October and November 2017
9 test-subjects
Interior
Exterior

## Slide 16: Inferred Personalized Profiles

## Slide 17: Prediction Performance
Proposed
Logistic regression
  S. Lee, P. Karava, A. Tzempelikos, I. Bilionis. “Inference of thermal preference profiles for personalized thermal environments with actual building occupants.” Building and Environment, 2019, 148:714-729.
  S. Lee, I. Bilionis, P. Karava, A. Tzempelikos. “A Bayesian approach for probabilistic classification and inference of occupant thermal preferences in office buildings.” Building and Environment, 2017, 118:323-343.

## Slide 18
Smart User-Interface

## Slide 19: Smart User-Interface
Temperature
Prefer warmer
Satisfied
Prefer cooler
Regular or random feedback requests
    Requesting occupants’ thermal comfort related responses
    Ideal way to minimize bias
    Intrusive and not practical in real buildings

## Slide 20: Smart User-Interface
  Few “Satisfied” responses
  Less data points from relatively comfortable conditions
Temperature
Prefer warmer
Satisfied
Prefer cooler
Participatory interface
    Voluntarily provided/submitted feedback when occupants want
    Participation, a type of behavior, could be affected by multiple factors (comfort/discomfort, workload, interface design, control logic, expectation)
    Sampling bias & cannot guarantee collection of necessary data

## Slide 21: Smart User-Interface
  Practical and effective feedback collection strategy
  Mainly rely on occupants’ participation (participatory responses)
  How to resolve the sampling bias issue
  Additionally request responses only when they are truly needed to learn effectively (smart request algorithm)
  How to quantify the expected value (information gain) of a request

## Slide 22: Experiment
Mar. – Apr. 2019
Three private offices
Five test-subjects
Two experimental setups

## Slide 23: Experiment
Setup 1: request
Pre-determined setpoint schedules
Feedback request every 30 minutes
Requested preference data
Sch. | 1st | 2nd | 3rd | 4th | 5th | 6th | Lunch Break | 7th | 8th | 9th | 10th | 11th | 12th
1 | 25 | 24.5 | 24 | 23.5 | 23 | 22.5 |  | 22 | 21.5 | 21 | 20.5 | 20 | 19.5
2 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 |  | 22.5 | 23 | 23.5 | 24 | 24.5 | 25
3 | 27 | 26.5 | 26 | 25.5 | 25 | 24.5 |  | 24 | 23.5 | 23 | 22.5 | 22 | 21.5
4 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24 |  | 24.5 | 25 | 25.5 | 26 | 26.5 | 27
Mar. – Apr. 2019
Three private offices
Five test-subjects
Two experimental setups
Setup 2: participatory
Participatory interface (no feedback request)
Temperature setpoint rule
    “Prefer cooler” → decrease by 0.5 °C
    “Satisfied” → no setpoint change
    “Prefer warmer” → increase by 0.5 °C
Initial temperatures (25, 22.5, 20 °C)
Participatory preference data

## Slide 24: Experiment

## Slide 25: Resolving the Sampling Bias Issue
Requested data (no sampling bias)
Participatory data (sampling bias)
Participatory data + Updated model
  To deal with the sampling bias and properly learn an occupant’s thermal preference with participatory data
  Revise the model structure to learn not only one’s preference but also how active the person is in using the interface.
Preference
Participation
1
2
3
1
2
3
Prediction error (expected cost)
Predictive probability distortion due to the sampling bias
Properly maintained uncertainty

## Slide 26: Smart Feedback Request Algorithm
Request occupants’ feedback, from time to time, when they are needed, to ensure or expedite the learning
Quantify the expected value (i.e., information gain) of requesting a response
Theory of Bayesian design of experiments provides a mathematical approach to solve the problem
Notes: 𝐷_𝐾𝐿 (also called relative entropy) is a measure of how one probability distribution is different from the other

## Slide 27: Smart Feedback Request Algorithm
Subject 1
Subject 1
Added seven requested responses collected between 21.5 - 22.5 °C
Value of a feedback request at given temperature changes
Expected information gain (expected KL divergence)
Expected information gain (expected KL divergence)

## Slide 28: Smart Feedback Request Algorithm
Request Only | 24
Proposed | 14.66
The average number of feedback requests in the scenarios
  S. Lee, P. Karava, A. Tzempelikos, I. Bilionis. “A smart and less intrusive feedback request algorithm towards human-centered HVAC operation.” Building and Environment, 2020, 184:107190.
Expected KL Divergence

## Slide 30: Measurements vs. EnergyPlus Results
Create datasets from the FRP for empirical validation of simulation tools, which has limited input uncertainty compared to real buildings.
Provide modeling Input document + operational data
Demonstrate with a detailed EnergyPlus model

## Slide 31: Measurements vs. EnergyPlus Results – Room Temperature
Room air temperatures [°C]
Temperatures from the EnergyPlus model do not match the corresponding measurements
Decided to investigate envelope material & construction properties

## Slide 32: Material Properties
 | Layers: exterior to Interior | Thickness |  | Conductivity |  | Density |  | Specific Heat |  | Thermal Resistance | 
 |  | m | inch | W/m-K | BTU.in/hr.ft2.F | kg/m3 | lbs/ft3 | J/kg-K | BTU/lb∙°F | m2-K/W | ft2·h·°F/Btu
Exterior wall | Face brick (EnergyPlus Library) | 0.10 | 4.00 | 0.89 | 6.17 | 1920.00 | 119.86 | 790.00 | 0.19 |  | 
 | Air Space (ASHRAE 90.1) |  |  |  |  |  |  |  |  | 0.16 | 0.90
 | Concrete Block Grout Filled only for 30% of the wall | 0.20 | 7.87 | 1.13 | 7.84 | 1218.00 | 76.04 | 920.00 | 0.22 |  | 
 | Gypsum | 0.02 | 0.62 | 0.16 | 1.11 | 784.90 | 49.00 | 1090.00 | 0.26 |  | 
 | Batt insulation (w. metal stud) - ASHRAE 90.1-2007 Effective R_value at 16 in o.c. | 0.09 | 3.50 | 0.09 | 0.64 | 4044.80 | 252.80 | 712.66 | 0.17 |  | 
 | Gypsum | 0.02 | 0.62 | 0.16 | 1.11 | 784.90 | 49.00 | 1090.00 | 0.26 |  | 
Exterior wall for 104 | Face brick (EnergyPlus Library) | 0.10 | 4.00 | 0.89 | 6.17 | 1920.00 | 119.86 | 790.00 | 0.19 |  | 
 | Air Space (ASHRAE 90.1) |  |  |  |  |  |  |  |  | 0.16 | 0.90
 | Concrete Block Grout Filled only for 30% of the wall | 0.20 | 7.87 | 1.13 | 7.84 | 1218.00 | 76.04 | 920.00 | 0.22 |  | 
 | Polyurethane (C.C. Spray Foam) | 0.05 | 2.00 | 0.02 | 0.17 | 32.00 | 2.00 | 920.00 | 0.22 |  | 
 | Blown in cellulose with steel stud | 0.09 | 3.50 | 0.09 | 0.64 | 4044.80 | 252.80 | 712.66 | 0.17 |  | 
 | Gypsum | 0.02 | 0.62 | 0.16 | 1.11 | 784.90 | 49.00 | 1090.00 | 0.26 |  | 
Exterior wall for 204 | Face brick (EnergyPlus Library) | 0.10 | 4.00 | 0.89 |  | 1920.00 | 119.86 | 790.00 | 1.89 |  | 
 | Air Space (ASHRAE 90.1) |  |  |  |  |  |  |  |  | 0.16 | 0.90
 | Concrete Block Grout Filled only for 30% of the wall | 0.20 | 7.87 | 1.13 | 7.84 | 1218.00 |  | 920.00 | 0.22 |  | 
 | Gypsum | 0.02 | 0.62 | 0.16 | 1.11 | 784.90 | 49.00 | 830.00 | 0.20 |  | 
 | Batt insulation (w. metal stud) - ASHRAE 90.1-2007 Effective R_value at 16 in o.c. | 0.09 | 3.50 | 0.09 | 0.64 | 4044.80 | 252.80 | 712.66 | 0.17 |  | 
 | Polyiso rigid Foam Board | 0.05 | 2.00 | 0.03 | 0.18 | 32.00 | 2.00 | 920.00 | 0.22 |  | 
 | Gypsum | 0.02 | 0.62 | 0.16 | 1.11 | 784.90 | 49.00 | 830.00 | 0.20 |  | 

## Slide 33: Sensors in the Walls
Temperature
Heat flux
Interior
Exterior
Gypsum
Batt Ins.
Concrete block
Air gap
Brick

## Slide 34: Wall Material Property Estimation 1-D Finite Difference heat conduction model
Internal node heat diffusion equation
discretization
Node temperatures
Boundary conditions
Process noise
Unconsidered factors influencing the dynamic
Model imperfection
Measurement noise
20 nodes (3 in gypsum, 6 in insulation, 10 in concrete block, 6 in face brick)

## Slide 35: Wall Material Property Estimation 1-D Finite Difference heat conduction model
Prior distributions for the other material properties (Gamma)
  mean: ~EP input values
  95% interval: ~30% of mean
Prior distribution for the density of the batt insulation layer (Gamma)
  Very flat hierarchical
~30% of mean
mean
Prior distribution for the density of the batt insulation layer (1/1000)

## Slide 36: Estimation Data – 206 South Wall
Surface Temperatures
Heat Flux
Surface Temperature [°C]
Heat Flux [W/m2]

## Slide 37: Estimation Results – 206 South Wall
R-value computed with median values = 3.625 [m2-K/W]
Air R
[m2-K/W]
Cp
[J/kg-K]
ρ
[kg/m3]
k
[W/m-K]
Gypsum
Batt
Gypsum
CMU
Face Brick

## Slide 38: Estimation Results – 206 South Wall
1
2
3
1
2
3
Median values of the root of the diagonal components in the process noise covariance matrix: 0.00189 – 0.413
Median values of the root of the diagonal components in the Measurement noise covariance matrix: 0.408, 0.00712, 0.0124
Node temperatures
Boundary conditions
Process noise
Unconsidered factors influencing the dynamic
Model imperfection
Measurement noise

## Slide 39: Limitations

## Slide 40: Limitations
May not represent the average heat flux/temperatures
  Measured heat flux is higher than the average
  Measured temperatures are closer to the exterior temp

## Slide 41: Potential Solutions?
The objective: provide material & construction properties
The problem: in-situ measurements are function of not only the material & construction properties but also the geometry
Potential solutions
  Install sensors far from edges – how to ensure that the measuring location is good enough to ignore the edge effects
  Bayesian estimation with a 2D or 3D heat conduction model and uncertain boundary conditions
  Any others?